## Scenarios
Potential Metering Scenarios for MA Utilities
I) AMR (mobile) Only (NU/NGRID SQ)
A) Swap Inidividual Meters for TOU--Drive By
2) Enhanced AMR
A) Home Area Network/Software (NSTAR Pilot)
B) Fixed External Area Network/Software
C) Swap Inidividual Meters for TOU--Wireless
3) Bridge AMI (new ITRON meter)
A) AMR (mobile) Mode
B) AMI (network) Mode
4) Unitil's AMI
5) Full AMI
6) AMR & Direct Load Control

## Functionality
Metering-Related Functionality
| Customer-Facing: | [7 empty] | Grid-Facing:
Scenarios: | Drive-By Meter Reading | Remote Meter Reading (at office) | TOU Register | Interval Data | Daily Read (at office) | On-Demand/"Real-Time" Meter Reading | Communication to Meter | Communication capability in meter to customer equipment (appliances, thermostats, vehicles) | Remote Service Connect/ Disconnect Switch | Voltage Reading | Power Quality Reading | Outage Identification & Restoration Notification | Planning Data (snap-shot demand reads system read) | Sub-Metering Capability (e.g., for EV recharging)
I) AMR (mobile) Only (NU/NGRID SQ) | Yes | No | No | No | No | No | One-way | No | No | No | No | Not readily | No
A) Swap Individual Meters for TOU--Drive By | Yes | No | Yes | No | No | No | One-way | No | No | No | No | Not readily | No
2) Enhanced AMR
A) Home Area Network/Software (NSTAR Pilot) | Yes | Maybe | Maybe | No | Maybe | Maybe | One-way | Yes | No | No | No | Maybe | Limited
B) Fixed External Area Network/Software | Yes | Yes | Yes | Yes | Yes | Possible | One-way | Maybe | No | No | No | Yes | Yes
C) Swap Individual Meters for Wireless Meters | NA | Yes | Yes | Yes | Yes | Maybe | One-way/two-way maybe | Yes (w/chip) | No | Yes | Limited | Not readily | Yes
3) Bridge AMI (new ITRON meter)
A) AMR (mobile) Mode | Yes | No | Yes | Yes | No | No | Limited two-way | Yes (w/chip) | Yes | Not readily | Not readily | Not readily | No
B) AMI (network) Mode | NA | Yes | Yes | Yes | Yes | Possible | Two-way | Yes (w/chip) | Yes | Yes | Yes | Yes | Yes
4) Unitil's AMI | N/A | Yes | Yes (can reprogram remotely) | No | Yes | No | Two-way | Yes (w/chip) | Yes | Yes | Yes | Yes | Yes
5) Full AMI | NA | Yes | Yes (can reprogram remotely) | Yes | Yes | Possible | Two-way | Yes (w/chip) | Yes | Yes | Yes | Yes | Yes
6) AMR & Direct Load Control | Yes | No | No | No | No | Meter No/DLC maybe | Either to the DLC device | No | No | No | No | No | No
Notes:
If NU customers currently opt into a TOU rate, put in different AMR meter (w/wireless capability w/interval data capability or 3rd chanel to read on/off peak--manually set time periods)
Large customers already have meters capable of interval data
Relying on Enhanced AMR via home internet platform not reliable for billing (data isn't stored)
Two way communiction means can remotely program meter and/or provide info thru meter to customers
DLC should consider enabling all options: utility, 3rd party, customer
Enabling DLC, Demand Response, & DG/EV/Storage columns are facilitated thru functions identified in other columns--probably delete these columns
Consider better defining or deleting Sub-Metering and DGA columns or better define and then complete
Columns M-P & V not populated as WG not sure they represent core "functionality" of meters
Note on G17: Eisfeller, Justin: System is capable of a remote on-demand usage read (not interval data) which takes several minutes to retrieve. System is also capable of "streaming data" with an upgrade but is not revenue grade information due to potential data gaps.
Note on J17: Eisfeller, Justin: system is capable but would require a new meter installation that has disconnect capability.
Note on K17: Eisfeller, Justin: This is meter dependant. Retrofitted mechanical meters are not capable, but newer electronic meters are.
Note on L17: Eisfeller, Justin: Can get outage and momentary outage infromation from every meter. Can get additional PQ data from electronic meters.

## Inremental Functionality
Incremental Metering Functionality
| Customer-Facing | Grid-Facing
AMR | Drive-By Meter Reading; One-Way Communication | Outage Detection possible (by drive by)
Enhanced AMR (w/HAN) | AMR PLUS Communication to Customer Equipment and MAY enable Remote Meter Read, TOU Register, Daily & Real-Time Meter Read | MAY enable Outage ID & Restoration Notification
Enhanced AMR (w/Fixed Network) | AMR PLUS Remote Meter Read, TOU Register, Intervial Data, Daily Read, and MAY also enable Real Time Data Read, Communication to Customer Equipment | Outage ID & Restoration Notification, and Planning Data
Full AMI | AMR (w/Fixed Network) PLUS Real Time Data Read, Two-Way Communication to Meter, Communication to Customer Equipment, | AMR (w/Fixed Network) PLUS Remote Service Connect/Disconnect Switch, Voltage Reading, Power Quality Reading
Note: See Functionality tab for full functionality listings for each scenario, and for functionality for other variation scenarios including Bridge Meters and Unitil's AMI

## Functionality & Applications
Functionality & Clean Energy/Other Applications
Which of the following meter functionality helps enable the various clean energy and other applications?
| Customer-Facing: | [7 empty] | Grid-Facing:
| Drive-By Meter Reading | Remote Meter Reading (at office) | TOU Register | Interval Data | Daily Read (at office) | On-Demand/"Real-Time" Meter Reading | Communication to Meter | Communication capability in meter to customer equipment (appliances, thermostats, vehicles) | Remote Service Connect/ Disconnect Switch | Voltage Reading | Power Quality Reading | Outage Identification & Restoration Notification | Planning Data (snap-shot demand reads system read)
Direct Load Control
Demand Response
Distributed Generation
Electric Vehicles/Recharging
Storage
Other??

## Definitions
Term | Definition
Drive-by Meter Reading | Meter reading accomplished by an employee with a truck that receives radio transmissions from customers' meters.
Remote Meter Reading | Meter reading accomplished through a wireless communication system that does not require field visits.
TOU Register | A meter functionality whereby the meter stores customer electricity usage information in specific time bands set by the utility. Depending on the meter and the utility's communication system, a TOU register may or may not be able to be changed without a field visit. A TOU register is necessary for TOU rates.
Interval Data | A meter functionality that captures hourly (or shorter) usage information as part of its regular meter reading activity that is billing grade.
Daily Read | A meter functionality that captures the daily electricity usage of a customer in certain increments of time without field visits.
On-Demand Real-Time Meter Reading | A meter functionality whereby the utility can target and read any meter on its system remotely upon demand.
Two-Way Communication | A meter with two-way communication can send and receive information to and from the utility without field visits.
Direct Load Control | Direct load control is a function of communication between the customer, the utility or a third-party and a specific device to alter the device’s operation, usually central air, pool pump, or hot water heater, etc. Direct load control can work with any type of meter.
Demand Response | Reducing usage at certain time periods in response to a signal.
Sub-Metering Capability | The capability to have a separate or "sub" meter that operates independently of the main meter at the customer's locus.
Remote Service Disconnect Switch | A "turn on" / "turn off" switch for a customer's electric power.
Voltage Reading | A meter functionality whereby the utility can detect a specific customer's voltage level At present, this functionality requires an AMI meter as well as additional equipment in the utility's distribution and substation systems.
Power Quality Reading | Functionality that measures a customer's outages or interruptions of electric service of less than one minute.
Outage Identification and Restoration Notification | A functionality whereby the meter notifies the utility of a power outage or the restoration of power to a specific customer.
Planning Data (Snapshot) | AMI systems typically have the ability to gather interval data for every customer that can be used to model the system for planning studies. These system model typically look at the “peak hour” scenario and are used to look at potential loading and voltage concerns on a system and contingency analysis (how might you restore a faulted system while maintain voltage and loading) for different growth scenarios. Unitil’s AMI system is not capable of providing interval metering data without an upgrade but is capable of capturing loads at every meter for a specific timeframe (i.e. tomorrow at 5pm). This load data serves the same purpose as the interval data would for developing a planning model that incorporates actual loading at every customer location. Having customer loads at a customer granularity level allows for very accurate modeling which provides the potential for capturing system issues earlier than you would making traditional loading assumptions. It also provides for better growth estimates which might allow for postponement of a particular infrastructure upgrade project.
Distributed Grid Automation | Not defined at the February 7th meeting.

## Cost
Residential Meter Costs
| Meter (equipment) Costs | Installation Costs | Home Area Network Enablement | Software & Network Infrastructure | Other Smart Grid Infrastructure (OMS, DMS, GIS) | Total Cost (1) | DLC at Device (for interested customers) | Annual O&M (as percent of capital cost) | Other Cost Factors
I) AMR Only (NU/NGRID SQ) | $30-50 | $20-40 | NA | 2 | NA | $52-92 | $100-150 | 10-30%
A) Swap Individual Meters for TOU--Drive By | 120 | $20-40 | NA | 2 | NA | $142-162 | $100-150 | 10-30%
2) Enhanced AMR
A) Home Area Network/Software | $30-50 | $100-200 | $125-175 | 2 | NA | $257-422 | $100-150 | 10-30%
B) Fixed Area Network/Software | $30-50 | $20-40 | NA | $15-30 | NA | $65-120 | $100-150 | 10-30%
C) Swap Individual Meters for TOU--Wireless | $300-600 (C&I only) | $20-40 | NA | 2 | NA | NA | $100-150 | 10-30%
3) Bridge AMI (new ITRON meter)
A) AMR (mobile) Mode | 120 | $20-40 | $125-175 | 2 | NA | $167-207 | $100-150 | 10-30%
B) AMI (network) Mode | 120 | $20-40 | $125-175 | $50-125 | $50-190 | $265-500 | $100-150 | 10-30%
4) AMI (Unitil SQ) | $70-150 | $20-40 | $75-150 | $50-125 | $50-190 | $265-655 | $100-150 | 10-30%
5) Full AMI (2) | $80-150 | $20-40 | $125-175 | $50-125 | $50-190 | $325-680 | $100-150 | 10-30%
6) AMR & Direct Load Control |  |  |  | $5-10 |  |  | $100-150 | 10-30%
Notes:
(1) The Total Costs are simply a total of the min-max individual costs. Actual upgrade costs will vary based on functionality deployed.
(2) Ranges on AMI in part related to different functionality
(3) Cost estimates based on combination of ITRON supplied cost, and MA utility experience
(4) In 3B if Bridge Meter already installed in "mobile" mode, no incremental equipment or labor cost to switch to AMI (network) mode
(5) Row 2A is based on NSTAR pilot costs, scale deployment could be different
(6) Software/Network Infrastructure cost relatively fixed, and likely lower cost/meter for large systems than small
(7) Other Smart Grid Infrastructure can vary significantly depending on pre-existing infrasturcture and what other options to pursue
and based on ITRON's analysis of other jurisdictions
(8) For DLC end costs/installation same, but communications cost vary significantly--i.e., likely less expensive for AMI

## Cost Caveats
This analysis was conducted as part of the Grid Modernization Working Group, and the facts, assumptions, and analysis contained within this spreadsheet were not subject to the process required for agency decision-making set forth in the Administrative Procedure Act. Accordingly, this analysis is for illustrative purposes only and should not be relied upon for any Department decision or order unless the facts, assumptions, and analyses relied upon are verified through a separate Department process conducted consistently with the Administrative Procedure Act and the Department’s regulations as codified in 220 CMR et. seq.
This analysis in the spreadsheet does not account for the risk to each utility's system that implementing the scenarios identified within could create. Specifically, at the February 7th meeting, NSTAR/NU expressed concern that the dramatic changes necessary to implement a new metering system could create significant reliability or billing issues.
This analysis does not include an analsyis of the costs or benefits of targeting a specific subsection of customers for customer-facing upgrades. Targeting those customers who have the greatest potential to reduce their peak period electricity usage (for instance, customers with central air conditioners that use a high volume of load at peak periods or customers who are interested in grid modernization technology and are thus most likely to remain engaged) may be more cost effective than an "all customers" approach.
Note: These 3 caveats were drafted by the AG and not yet reviewed by the WG